| ASEAN Engineering Journal |  |  |  | Full Paper |
| --- | --- | --- | --- | --- |
| STUDI KOMPARASI TUNING PID PADA LOOP LEVEL CONTROL 91LIC538 SISTEM AMINE CIRCULATION DI UNIT 91 KILANG SRU PT PERTAMINA PATRA NIAGA RU IV CILACAP Bagaskara Program Studi S1 Teknik Elektro, Fakultas Teknik, Universitas Diponegoro |  |  | Article history Received X Month 202Y Received in revised form XA Month 202Y Accepted XB Month 202Y Published online XB Month 202Y *Corresponding author maman@uxm.edu.my Please provide an official organisation email of the corresponding author |  |
| Graphical abstract a. Graphical Abstract is a compulsory item and should represent the content of the article. Please change this picture with your own graphical abstract. |  | Abstract Level control loops play an important role in maintaining process stability and preventing unsafe operating conditions caused by inlet and outlet flow variations. This internship report presents a comparative study of PID tuning for the 91LIC538 level control loop in the Amine Circulation system at Unit 91 SRU Refinery of PT Pertamina Patra Niaga RU IV Cilacap using Honeywell DCS historian data. The analysis was performed on the event window of January 28, 2026, 02:28–03:28 using SP, PV, and OP signals. The study includes performance evaluation of the existing controller from historian data, process model identification using a First Order Plus Dead Time (FOPDT) approach, controller parameter calculation using the Ziegler Nichols process reaction curve method, and comparative MATLAB simulation using a 1% setpoint step test. The identified model parameters are Kp 0.468, τ 26.20 s, and θ approximately 0 s, with validation results RMSE 0.72% and R² 0.79. The existing DCS controller is a PI controller with Kc 2.00 and Ti 5 min, while Ziegler–Nichols tuning yields a PID controller with Kc 13.44, Ti 10 s, and Td 2.5 s. Simulation results show that Ziegler Nichols tuning improves tracking speed with rise time 6.15 s and settling time 32.26 s compared to the existing controller with rise time 993.90 s and settling time 1973.44 s, and reduces error indices with IAE 4.55 %·s and ISE 1.91 %²·s compared to the existing controller with IAE 320.51 %·s and ISE 89.55 %²·s. However, Ziegler Nichols tuning increases control effort with maximum ΔOP 13.78% and TVOP 11.99 and introduces an overshoot of 8.82%. Therefore, Ziegler Nichols tuning provides a significant improvement in setpoint tracking, but further refinement such as detuning and output limiting is recommended prior to field implementation. Keywords: PID, 91LIC538, Amine Circulation, FOPDT, Ziegler Nichols, MATLAB, Control Effort.. |  |  |
|  |  | © 2022 Penerbit UTM Press. All rights reserved |  |  |

© 2024 Penerbit UTM Press. All rights reserved.